# Provision of Colocation Services for Btr Operations

Tenders Monitor Africa-Asia

January 25, 2021 Monday

Copyright 2021 Al Bawaba. Provided by Syndigate Media Inc. All Rights Reserved

Length: 1712 words

Body

Company  : BUREAU OF THE TREASURY

Address : Ayuntamiento Building, Cabildo St., cor. A. Sorian

Intramuros, Manila

Manila

Metro Manila 1002

Attn: Mr. Clarence Bolante Bunan, Administrative Officer III

Tel: +63-2-6632206

Fax: +63-2-5247008

Email : cbbunan@treasury.gov.ph

Country : Philippines

Location :  Philippines

Tender_No : 2021-01-0026 SAD

Value : PHP 907000

Dead line : 2021-01-28

Local International : International

Funding Agency : No

Description :  Request for Quotation (RFQ): Provision of Colocation Services for Btr Operations

Closing Date / Time: 28/01/2021 12:00 PM

Area of Delivery: Metro Manila

Procurement Mode: Negotiated Procurement - Small Value Procurement (Sec. 53.9)

Brief: Terms of Reference

Project Title

Provision of Colocation Services for Btr Operations

Description

The Project Calls for the Procurement of Data Center Colocation Services for the Bureau of the Treasury (Btr) Computer Operations, Including the Provision of Internet Access Service at the Colocation Site.

Approved Budget of the Contract

The Agency Budget Estimate for the Project is Nine Hundred Seven Thousand Pesos (Php907,000.00), Inclusive of All Applicable Taxes.

Implementation Start Date and Duration of the Contract

1. Implementation Start Date must be within 60 Calendar Days after Receipt of Notice to Proceed or Purchase Order.

1.1. A "Certificate of Acceptance" shall be Issued after the Ten (10) Working Day Testing Period, Provided that the following Conditions are Met:

1.1.1. Completion of Required Tests of All Hardware and Software Requirement of the Project to Ensure Operationability of the Facility.

1.1.2. Average Latency of the Ias should not Exceed:

1.1.2.1. 80milliseconds Average Round Trip from Btr Site to Isp Port

1.1.2.2. 200milliseconds Average Round Trip from Isp Port to Us/International Port.

1.1.2.3. Stable Internet Service Connection.

2. Duration of the Contract

2.1. Contract Period shall be One (1) Year from the Start Date of Service Implementation.

2.1.1. The Effective Start of the Required Service shall be Based on the Issuance of the Certificate of Acceptance by Btr-Miss.

2.1.2. If the Contract is not Renewed on Time Due to Possible Delay in the Procurement Process, The Service shall be Automatically Deemed Extended and shall be Subjected to Month-To-Month Payment to be Based on the Contract Monthly Service Fee.

Scope of Work and Technical Specifications

Purchaser's Specifications Supplier's Specification

The Minimum Requirement Specified in this Scope of Work shall be Complied with. Non-Compliance with These Requirements is a Ground for Disqualification.

3. Colocation Services

3.1. Requirement

3.1.1. One (1) Full Rack with 20a Rated Power

3.1.2. Copper Cross Connection

3.1.3. Other Services Required to Ensure Operation Ability of the Collocated Equipment.

3.2. Responsibilities:

3.2.1. Btr

3.2.1.1. Shall be Responsible for the Provision of Servers, Top of Rack Switches and Security Equipment Necessary to Securely Run its Applications.

3.2.1.2. Shall be Responsible for the Installation and Configuration of Servers and Security Equipment.

3.2.2. Service Provider

3.2.2.1. Shall be Responsible for the Installation and Provision of Cabling (Up to the Assigned Rack) Necessary to Connect Btr Servers to the Internet and Other Telecommunication Lines.

3.2.2.2. Shall be Responsible for the Relocation of the Btr Equipment in the Event that the Colocation Facility was Compromised at No Cost.

3.3. Service Level Requirement

3.3.1. Provision of 24x7 Support Services.

3.3.2. Must Provide Single Point of Contact for All Technical Issues.

3.3.3. Rebates as a Result of Downtimes or Service Disruption must be Reflected on the following Month Billing.

3.3.4. Any Maintenance Service Incurred during the Contract Period shall be at No Cost to Btr.

3.3.5. Btr must be Notified in 3 Days Advance for Any Scheduled Maintenance Activities or Service Interruption.

3.3.6. Must Submit Corresponding Service Level Agreement (Sla) Document to Include Service Level Requirements with a Corresponding "Performance Credit" or "Rebate" in Favour of Btr should There be Any Disruption of Service.

3.4. Colocation Environmental Requirements

3.4.1. Building Structure

3.4.1.1. Must be Designed in Accordance with the National Structure Code of the Philippines Using the Highest Consideration for Building Construction, Maximum Security and Safety.

3.4.1.2. Must be at Least Seismic Zone 4 Compliant, Can Withstand at Least an Intensity 8 Earthquake and should not be More than Five (5) Years Old from the Time it was Built.

3.4.1.3. For Diversity and Alternative Sites in the Event that the Client would Require its Data Center (Dc) to be Extended over to an Alternative Location, The Provider must have Data Centers Located and Operated across the Country's Major Business Hubs, Like in the Cebu and North Luzon.

3.4.1.4. The Dc must be Compliant to the Dc Tier 3 Requirements.

3.4.1.5. The Dc Provider must be Able to Guarantee an Sla of at Least 99.99% Uptime.

3.4.1.6. The Dc Provider must be the Owner of the Facility and not a Leased Property.

3.4.1.7. The Dc must be Concurrently Maintainable, Allowing the Ability to Shut-Down Any Particular Electrical Component for Maintenance & Testing without Requiring that the Critical Load will be Offline.

3.4.1.8. The Dc must be Able to Withstand Wind Velocity Consideration of 250kph.

3.4.1.9. The Floor Loading Capacity must be at Least 250psf.

3.4.2. Heating, Ventilation and Air-Conditioning (Hvac)

3.4.2.1. Must Provide a Minimum of N+1 Configuration for Major Mechanical Equipment Such as Pumps, Cooling Towers, And Condensers.

3.4.2.2. Must Provide a Minimum of N+1 Configuration for Crac Units.

3.4.2.3. The Cracs must be Located in Separate Rooms with Separate Entry and Maintenance Works from the Server Farm to Lessen Security Risks to Client Equipment & Data.

3.4.2.4. Cracs must have Dual Power Supplies to Eliminate Single Point of Failure.

3.4.3. Uninterruptible Power Supply

3.4.3.1. Must Provide Separate Ups Systems for the it Load and Cooling Load.

3.4.3.2. Must Provide a Minimum of N+1 Configuration for Ups, And 15 Min Back-Up for Crac Supply.

3.4.3.3. Must Provide a Minimum of 2n Configuration and 15 Min Back-Up for Client Racks Supply.

3.4.3.4. Each Ups must have its Own Static Transfer Switch (Sts) so it can Operate Independently.

3.4.3.5. Ups Batteries should have a Separate Room for Added Protection.

3.4.4. Backup Generators

3.4.4.1. Must Provide a Minimum of 2n Configuration to Support the Power Requirements of the Data Center.

3.4.4.2. In the Case of a Disaster, The Generators must be Able to Provide Power for at Least Four (4) Days of Continuous Operation without Commercial Power.

3.4.4.3. The Generator Sets must be Data Center Grade Allowing for it to Run Continuously without the Need to Rotate the Units to Cool it down.

3.4.4.4. The Generator Sets must have Multiple Fuel Storage Tanks with Multiple Pumps and Piping System to Eliminate Single Point of Failure.

3.4.5. Fire Suppression System

3.4.5.1. Must Provide an Environment Friendly Gas-Based Fire Suppression System at the Server Farm, Equipment Room and Telco Rooms.

3.4.5.2. The Server Farms must have Discharge Nozzles and Smoke Detectors Both at the Ceiling and under the Raised Flooring.

3.4.5.3. The Facility must have Very Early Warning Smoke Detection System.

3.4.6. Raised Floor Specifications

3.4.6.1. Must have Raised Floor Panels with at Least 61cm X 61cm (24" X 24") Dimension.

3.4.6.2. Must have a Minimum of 0.7m Vertical Clearance under-Floor.

3.4.6.3. Must have at Least 250psf Floor Loading Capacity with Max Rack Weight of 1,500 Kg.

3.4.6.4. The Raised Floor must have Seismic Bracing to Provide Additional Stability in the Event of an Earthquake.

3.4.7. Network Backbone Architecture

3.4.7.1. To Avoid Complete Dependence to a Single Telco Carrier, The Provider must be Carrier-Agnostic.

3.4.7.2. Must have a Minimum of Three (3) Carrier Service Entrance, Allowing for a Resilient (Multi-Carrier) Design Configuration.

3.4.7.3. Must have Minimum of Two (2) Diverse Cable Risers to the Server Farm up to the Rack Level.

3.4.7.4. The Data Center Network must be Software-Defined Network (Sdn) Ready.

3.4.7.5. Must have Meet-Me-Rooms Where Other Telco Providers can Provide Connectivity Requirements of the Clients. The Rooms must have Redundant Power for the Telco Equipment Cages.

3.4.8. Building Management System

3.4.8.1. The Provider must have Water Leak Detection (Wlds) Systems under the Raised Floor.

3.4.8.2. The Provider must have a Data Center Infrastructure Management (Dcim) that will Allow for a Reliable and Centralized Monitoring of the following Dc Equipment:

3.4.8.3. Electrical System Showing the Status (On/Off & Trip Position of Cb's), Essential Parameters, Utilization of Equipment Capacity and Branch Circuit Monitoring of each Server Rack Load.

3.4.8.4. Dcie / Pue Metering.

3.4.8.5. Ups & Batteries Status, Essential Parameters and Alerts.

3.4.8.6. Static Transfer Switch (Sts) Status, Essential Parameters and Alerts.

3.4.8.7. Air-Conditioning System Such as Chiller System and Crac's Status and Essential Parameters.

3.4.8.8. White Space Cold Aisles Temperature and Humidity Status and Alerts.

3.4.8.9. Water Leak Detection System Status and Alerts.

3.4.8.10. Fire Protection Status and Alerts.

3.4.8.11. Generator System Essential Parameters and Fuel Level Status.

3.4.9. Support Services

3.4.9.1. The Provider must have (At a Minimum) the following Capabilities:

3.4.9.1.1. 24 X 7 Helpdesk, Phone and Email Support;

3.4.9.1.2. Remote Hands; and

3.4.9.1.3. 24 X 7 Site Access to Customer

3.4.9.2. The Data Center must have a 24 X 7 Network Operations Center (Noc) that Provides Centralized Monitoring System.

3.4.9.3. The Noc should be Able to View each and Every Floor as Well as All the Rooms, Zero in on the Client's Particular Rack, Monitor its Temperature, Humidity, Heat Dissipation, Power Consumption and Even up to the Server Status Level.

3.4.9.4. The Noc must be Capable of Viewing a Representation of the Client Equipment Installed inside the Racks Making it Easier to do Rack Equipment Inventory and Monitoring.

3.4.10. Security

3.4.10.1. The Provider must have Multiple Layers of Security between the Main Entrance of the Facility and the Co-Located Racks for P

Document :  http://www.bidsinfo.com/adminexe/documents/-PH1~20210125-22803112.html

Classification

Language: ENGLISH

Publication-Type: Newspaper

Journal Code: 2106

Subject: PURCHASING & PROCUREMENT (90%); TREASURY DEPARTMENTS (90%); TENDER NOTICES (79%); TAXES & TAXATION (68%); BUDGET FORECASTS (66%); NEWS BRIEFS (54%)

Industry: TREASURY DEPARTMENTS (90%); INTERNET SERVICE PROVIDERS (89%); COMPUTER NETWORKS (87%); BUDGETS (78%); INTERNET & WWW (78%); SOFTWARE SERVICES & APPLICATIONS (78%); COMPUTER SOFTWARE (67%); DATA CENTERS (67%); BUDGET FORECASTS (66%)

Geographic: MANILA, PHILIPPINES (91%); PHILIPPINES (94%); ASIA (73%)

Load-Date: January 25, 2021

End of Document